CONTROLLED ENTERPRISE DOCUMENT TBT-26.03 ¦ Temporary Lighting And Gfci Protection MH Construction, INC Enterprise Management System Document family: TOOLBOX TALK LIBRARY Document title: TBT-26.03 ¦ Temporary Lighting And Gfci Protection Version: 1.0 ¦ Lifecycle: Rough Draft Use only after required functional, technical, field-usability, and approval gates are complete.

Control: Version 1.0 | Status Rough Draft | Author and Chief Editor: Matt Ramsey | Co-Editor: Todd Shoeff | Final Approver: Jeremy Thamert

# TBT-26.03: Temporary Lighting & GFCI Protection

CSI Division: Div 26 | OSHA Reference: 29 CFR 1926.405

Delivery: Mandatory for all crews utilizing temporary power on site.

## DIRECTIVE — Policy Standard

All 120-volt, single-phase, 15- and 20-ampere receptacle outlets on construction sites must have Ground-Fault Circuit Interrupter (GFCI) protection.

### GENERAL ORDER — Procedure

Temporary lighting strings must be suspended by their non-conductive molded hangers, not by the electrical wire itself. Bulbs must be protected by wire guards.

### Key Hazards & Mitigation (The 'What If'):

• Daisy-Chaining Cords: If a crew plugs three 100-foot extension cords together to reach a work area, the voltage drop will damage tools and create a fire hazard. Use a temporary spider box closer to the work.

• Missing Ground Prong: If an extension cord or tool is missing the third (ground) prong, it must be cut and thrown away. Do not plug it in.

• Water in the Box: If a temporary power box is sitting in a puddle after a rainstorm, do not touch it. Have the electrician elevate it and verify the GFCI is functioning.

#### FIELD INSTRUCTION — Execution

FIELD INSTRUCTION: Foremen must instruct crews to inspect all extension cords for cuts and missing ground prongs before plugging in today. Log attendance on MISH-F-10.1.

Attendance Roster (Log on MISH-F-10.1):

| Print Name | Signature | Company/Trade |
| --- | --- | --- |